## Cover sheet
Cover Sheet
Document | energy_power_wood_pellets_ccs_must_run.ad
Author | Kyra de Haan
Organization | Quintel
Legend
Cells | Intermediate (calculation)
Result
Manual input
Reference to manual input or data input
Tabs | Introductory
Dashboard
Research data
Sources
Results
Main calculations
Additional calculations
Output to csv

## Dashboard
This sheet summarizes all node attributes formatted in the way they are used by the Energy Transition Model. Use the Excel formulas to find the original data and sources for these numbers. You can also use this document to update the attribute value. Once you have finished updating, save this document and run rake import:node NODE="nodename" to update the node attributes on ETSource.
| Attribute | Unit | Value | Definition | Source
Technical
| availability | - | 0.9 |  | sourced from energy_power_ultra_supercritical_coal
| electricity_output_capacity | MW | 628 | Electricity output capacity | TNO, energy.nl
| input.wood_pellets | - | 1
| output.electricity |  | 0.361 | electrical efficiency | based on energy_power_ultra_supercritical_coal_ccs, sourced from datasets/nl2019/central_producers.csv
| full load hours | hours/year | 7500 |  | TNO
Cost
| initial_investment | euro | 1120000000 | Initial investment costs | Energymatters, Harvard
| ccs_investment | euro | 1092720000 | Additional initial investment cost for ccs | TNO, energy.nl
| cost_of_installing | euro | 0 | Installation cost | sourced from energy_power_ultra_supercritical_coal
| decommissioning_costs | euro | 0 | Decmmmissioning cost | sourced from energy_power_ultra_supercritical_coal
| fixed_operation_and_maintenance_costs_per_year | euro/year | 33584000 | Fixed operational and maintenance costs per year coal + CCS | Harvard, TNO, energy.nl
| variable_operation_and_maintenance_costs_per_full_load_hour | euro/FLH | 800 | Variable operational and maintenance costs (excl CCS) | sourced from energy_power_ultra_supercritical_coal
| variable_operation_and_maintenance_costs_for_ccs_per_full_load_hour | euro/FLH | 1256 | Additional variable operation and maintenance costs for CCS | TNO, energy.nl
| wacc | % | 0.07 | Weighted average cost of capital CCS technology | https://docs.energytransitionmodel.com/main/cost-wacc#commercial--proven-technologies-real-wacc-4
| takes_part_in_ets | yes=1, no=0 | 1
Other
| construction_time | years | 4 | Construction time of the plant | IEA, Harvard
| technical_lifetime | years | 40 | Technical lifetime of the plant | IEA, Harvard
| free_co2_factor | - | 0.9 |  | TNO, energy.nl
| ccs_capture_rate | - | 0.9 | CCS capture rate | TNO, energy.nl

## Research data
Parameter | Unit | Results | Energymatters | TNO, energy.nl | Harvard | Expert's opinion | IEA | Maasvlakte | Eemshaven | Comments
Technical
Electricity output capacity | MW | 628 | 600 | 628
CO2 capture rate |  | 0.9 |  | 0.9
full load hours |  | 7500 | 8000 | 7500
Other
Construction time | years | 4 |  |  | 4 |  | 4
Technical lifetime | years | 40 |  | 40 | 40 |  | 40
Costs
Initial investment costs for typical output MWe | euro | 1120000000 | [7 empty] | calculated value from Harvard
Additional investment costs CCS for typical output MWe | euro | 1092720000 |  | 753600000 |  | 1092720000 |  |  |  | value from expert's opinion is based on TNO source and corrected for inflation, these costs seem in line with the current additional investment costs for CCS
Fixed O&M costs total (coal + CCS) for typical output MWe | euro/year | 33584000 | [7 empty] | calculated value from Harvard & TNO, energy.nl
Variable O&M costs typical output MWe | euro/year | 6000000 | [7 empty] | calculated value from Harvard
Variable O&M costs typical output MWe | euro/FLH | 800 | [7 empty] | calculated value from Harvard
Additional variable O&M costs CCS typical output MWe | euro/year | 9420000 | [7 empty] | calculated value from TNO, energy.nl
Additional variable O&M costs CCS typical output MWe | euro/FLH | 1256 | [7 empty] | calculated value from TNO, energy.nl

## Sources
Definition on the sources
Type | Source | Country | Date published | Subject year | Date retrived | ETM Library URL | Link
| IEA | EU | 2010 | 2010 |  | http://refman.et-model.com/publications/1442 | http://www.iea.org/publications/freepublications/publication/projected_costs.pdf
Construction time
Technical lifetime
| Harvard | GER | 2010 | 2010 |  | http://refman.et-model.com/publications/1682 | http://www.hks.harvard.edu/hepg/Papers/2010/Michael_Hogan_May2010.pdf
Fixed operational and maintenance costs
Initial investment costs
Technical lifetime
Construction time
| Energymatters | NL | 2012 | 2012 |  | http://refman.et-model.com/publications/1937
Initial investment costs
| TNO, energy.nl | NL | 2020 | 2020 |  | https://refman.energytransitionmodel.com/publications/2192 | https://energy.nl/data/post-combustion-co%E2%82%82-capture-add-on-for-power-plants-solid-fuels/
Full load hours
Investment, O&M costs
CO2 capture rate
Typical scale
Producer price index | Trading economics, Eurostat | EU | 2023 | 2023

## Notes
Sources |  | Notes
|  | Electricity output capacity | 628 | MW | In this Node source analysis it is assumed that a powerplant of 800 MW without CCS is needed to obtain 637 MW output with CCS
|  | Full load hours | 7500 | h/y | All non-CCS related costs are therefore based on an 800 MW powerplant. All CCS-related costs are based on a powerplant with 637 MW
|  | Electricity production | 4710000 | MWh/y | With the calculated costs the powerplant capacity is shown.
|  | Electricity production without CCS | 6000000 | MWh/y
|  | Investment costs, fixed O&M and variable O&M |  |  | Costs excl CCS are assumed from Harvard source, additional costs for CCS are assumed from TNO factsheet, energy.nl
|  | Initial investment costs coal | 1400 | euro/kWe
|  | Additional investment costs CCS | 1200 | euro/kWe
|  | Fixed O&M costs coal | 20 | euro/kWe/yr
|  | Additional fixed O&M costs CCS | 28 | euro/kWe/yr
|  | Fixed O&M costs total (coal + CCS) | 48 | euro/kWe/yr
|  | Variable O&M costs coal | 1 | euro/MWh/yr
|  | Additional variable O&M costs CCS | 2 | euro/MWh/yr
|  | Initial investment costs for typical output MWe | 1120000000 | euro | 800 MW powerplant
|  | Additional investment costs CCS for typical output MWe | 753600000 | euro | 637 MW powerplant
|  | Additional investment costs CCS for typical output MWe (inflation corrected) | 1092720000 | euro | 637 MW powerplant
|  | Fixed O&M costs coal for typical output MWe | 16000000 | euro/year | 800 MW powerplant
|  | Additional fixed O&M costs CCS for typical output MWe | 17584000 | euro/year | 637 MW powerplant
|  | Fixed O&M costs total (coal + CCS) for typical output MWe | 33584000 | euro/year | 637 MW powerplant
|  | Variable O&M costs typical output MWe | 6000000 | euro/year | 800 MW powerplant
|  | Variable O&M costs typical output MWe | 800 | euro/FLH | 800 MW powerplant
|  | Additional variable O&M costs CCS typical output MWe | 9420000 | euro/year | 637 MW powerplant
|  | Additional variable O&M costs CCS typical output MWe | 1256 | euro/FLH | 637 MW powerplant
Energymatters |  | Investment costs | 1400 | €/kWe
p.1 |  | Typical scale | 600 | MWe
|  | Full load hours (electricity) | 8000 | h/y
TNO, energy.nl |  | full load hours | 7500 | h/y | 7500-8000 h/y
|  | technical lifetime | 40 | y | 30-40 y
|  | typical scale without CCS | 800 | MW | 500-1000 MW
|  | typical scale with CCS | 628 | MW | electrical efficiency 46% without CCS and 36.1% with CCS (sourced from energy_power_ultra_supercritical_coal)
Costs (provided as additional costs for CCS)
|  | Investement costs | 1200 | €/kWe | 700-1700 €/kWe, includes costs for CO2 capture, CO2 compression and utilitiy units
|  | Fixed operational costs (excl fuel) | 28 | €/kWe | include additional costs for maintenance, labour, administration insurance and taxes
|  | Variable costs | 2 | €/MWh | include additional chemicals, cooling water charges and waste disposal costs
|  | CO2 capture rate | 0.9 |  | 0.85-0.95
Expert opinion |  | Additional initial investment costs for CCS | 1500000000 | €/unit | approximate price for one typical unit
|  | Additional initial investment costs for CCS inflation corrected | 1740 | €/kWe | from the expert opinion the costs of TNO source should be corrected for inflation to determine the appropriate price
|  | Additional initial investment costs for CCS inflation corrected | 1092720000 | €/unit | these inflation corrected costs are more in line with the current costs for CCS
Trading Economics, Eurostat |  | Producer price index 2023 (compared to 2015) | 1.45
Harvard |  | Initial investment costs coal conventional | 1400 | €/kWe | 1400-1600 €/kWe
p.30 |  | Initial investment costs coal CCS | 2700 | €/kWe | 2700-2900 €/kWe
|  | Additional investment costs for CCS | 1300 | €/kWe
|  | Fixed O&M coal conventional | 20 | €/kWe | 18-22 €/kWe
|  | Fixed O&M coal CCS | 70 | €/kWe | 60-80 €/kWe
|  | Additional fixed O&M costs for CCS | 50 | €/kWe
|  | Variable O&M coal conventional | 1 | €/MWh
|  | Variable O&M coal CCS | 3 | €/MWh
|  | Additional variable O&M coal CCS | 2 | €/MWh
|  | Construction time | 4 | yr
|  | Lifetime | 40 | yr
IEA
p.43
| Lifetime | 40 | yr
p.44
| Construction time | 4 | yr