## Cover sheet
Cover Sheet
Document | buildings_space_heater_heatpump_surface_water_water_ts_electricity.converter.ad
Author | Koen van Bemmelen
Organization | Quintel
Legend
Cells | Intermediate (calculation)
Result
Manual input
Reference to manual input or data input
Tabs | Introductory
Dashboard
Research data
Sources
Results
Main calculations
Additional calculations
Output to csv

## Dashboard
This sheet summarizes all node attributes formatted in the way they are used by the Energy Transition Model. Use the Excel formulas to find the original data and sources for these numbers. You can also use this document to update the attribute value. Once you have finished updating, save this document and run rake import:node NODE="nodename" the button to update the node attributes on ETSource.
| Attribute | Unit | Value | Definition | Source
Technical
| input.ambient_heat | - | 0.697
| input.electricity | - | 0.303
| output.useable_heat | - | 1
| availability | - | 0 |  | Quintel assumption
| full_load_hours | - | 1750 |  | Quintel assumption
| electricity_output_capacity | MW | 0 | Electricity output capacity | No electricity output for this plant
| heat_output_capacity | MW | 4.4 | Heat output capacity
Cost
| initial_investment | euro | 4744522 | Initial investment costs
| ccs_investment | euro | 0 | Investment cost with ccs | No CCS unit for this plant
| cost_of_installing | euro | 0 | Installation cost | Quintel assumption
| decommissioning_costs | euro | 0 | Decommissioning cost | Quintel assumption
| fixed_operation_and_maintenance_costs_per_year | euro/year | 110639 | Fixed operational and maintenance costs per year
| variable_operation_and_maintenance_costs_per_full_load_hour | euro/FLH | 0 | Variable operational and maintenance costs | Quintel assumption
| variable_operation_and_maintenance_costs_for_ccs_per_full_load_hour | euro/FLH | 0 | Variable operational and maintenance costs for ccs | No CCS unit for this plant
| wacc | % | 0.04 | Weighted average cost of capital | Quintel assumption (see https://docs.energytransitionmodel.com/main/cost-wacc)
| takes_part_in_ets | yes=1, no=0 | 0 |  | Quintel assumption
Other
| construction_time | years | 0 | Construction time of the plant
| technical_lifetime | years | 30 | Technical lifetime of the plant
| free_co2_factor | - | 0 |  | Quintel assumption

## Research data
Parameter | Unit | Results | TNO | IF | Vesta | Comments
Technical
input.ambient_heat |  | 0.69697 | 0.78261 | 0.69697 |  | Chosen for IF value because TNO assumes collective system
input.electricity |  | 0.30303 | 0.21739 | 0.30303 |  | Chosen for IF value because TNO assumes collective system
Heat output capacity | MW | 4.4 | 4.4
Full load hours | hour | 1750 | 1750
Other
Land use | km2 | 0 |  |  |  | Quintel assumption
Construction time | years | 0 |  |  |  | Quintel assumption
Technical lifetime | years | 30 | 30
Costs
Initial investment costs | euro | 4744522 | 7012500 | 5497685 | 1723379.6296
Fixed operational and maintenance costs | euro/year | 110639 | 137500 | 118750 | 75666.6667
Fixed operational and maintenance costs | euro/KW/year | 25
Variable operational and maintenance costs | euro/FLH | 0 |  |  |  | Quintel assumption
Variable operational and maintenance costs | euro/MWh | 0 |  |  |  | Quintel assumption

## Sources
Definition on the sources
| Source | Country | Date published | Subject year | Date retreived | ETM Library URL | Link
| Functioneel ontwerp 5.0 Vesta MAIS | NL | 2021 |  | 2023-08-01 | https://refman.energytransitionmodel.com/publications/2145
| Aquathermal surface water factsheet | NL | 2018 |  | 2023-10-01 | https://refman.energytransitionmodel.com/publications/2173
| Kengetallen aquathermie | NL | 2019 |  | 2023-10-01 | https://refman.energytransitionmodel.com/publications/2174

## Notes
Source | Attribute (EN) | Attribute (NL) | Min value | Max value | Value | Unit | Comment | Data reference
Aquathermal surface water factsheet | Capacity | Jaarlijks geleverde energie | 0.01 | 0.04 | 0.025 | PJ |  | Figure A | Figure A
Aquathermal surface water factsheet | Full load hours | Vollasturen | 1500 | 2000 | 1750 | hours/year | Average of values mentioned in the table | Figure A
Aquathermal surface water factsheet | Technical lifetime | Afschrijftermijn |  |  | 30 | year |  | Figure A
Aquathermal surface water factsheet | Heat output capacity | Vermogen | 1.3889 | 7.4074 | 4.3981 | MW | 0.01-0.04 PJ mentioned in source taken as annual production based on mentioned full load hours | Figure A
Kengetallen aquathermie | SPF aquathermal surface water heat pump utility buildings | SPF TEO warmtepomp utiliteit | 2.7 | 3.9 | 3.3 | factor | Estimated from lines in graph based on 25000 GJ annual production | Figure B
Aquathermal surface water factsheet | SCOP aquathermal surface water heat pump utility buildings | SCOP TEO warmtepomp utiliteit |  |  | 4.6 |  | Mentioned in text, but based on collective system | Figure A
Aquathermal surface water factsheet | Investment costs aquathermal heat pump utility building | Kosten per aansluiting TEO warmtepomp utiliteit | 4150000 | 9875000 | 7012500 | eur/unit | Costs in mln €/PJ taken from 'current' values in table. Costs calculated with average heat output capacity (see above) | Figure A
Kengetallen aquathermie | Investment costs aquathermal heat pump utility building | Kosten per aansluiting TEO warmtepomp utiliteit | 5277777.7778 | 5717592.5926 | 5497685.1852 | eur/unit | Costs in €/kW estimated from lines in graph based on 25000 GJ annual production. Costs calculated with average heat output capacity (see above) | Figure C
Functioneel ontwerp 5.0 Vesta MAIS | Investment costs aquathermal heat pump utility building | Kosten per aansluiting TEO warmtepomp utiliteit | 960833.3333 | 1174351.8519 | 1067592.5926 | eur/unit | Based on minimum and maximum values of 'vaste kosten aanleggen TEO bron' en 'kosten per kW voor aanleggen TEO bron, using average heat output capacity calculated above. | Figure F
| Investment costs aquathermal storage | Kosten per aansluiting WKO bron | 590208.3333 | 721365.7407 | 655787.037 | eur/unit | Based on minimum and maximum values of 'vaste kosten aanleggen WKO systeem' en 'kosten per kW voor aanleggen WKO systeem', using average heat output capacity calculated above.
Kengetallen aquathermie | Annual operation and maintenance costs aquathermal heat pump utility building | Jaarlijkse onderhouds- en beheerkosten TEO warmtepomp utiliteit | 114351.8519 | 123148.1481 | 118750 | eur/unit/year | Costs in €/kW estimated from lines in graph based on 25000 GJ annual production. Costs calculated with average heat output capacity (see above) | Figure D
Aquathermal surface water factsheet | Annual operation and maintenance costs aquathermal heat pump utility building | Jaarlijkse onderhouds- en beheerkosten TEO warmtepomp utiliteit | 75000 | 200000 | 137500 | eur/unit/year | Fixed operational costs/year. Calculated using average capacity (see above) | Figure A
Functioneel ontwerp 5.0 Vesta MAIS | Annual operation and maintenance costs aquathermal heat pump utility building | Jaarlijkse onderhouds- en beheerkosten TEO warmtepomp utiliteit | 54976.8519 | 70125 | 62550.9259 | eur/unit/year | Based on 'onderhoudspercentage WKO-bron' and the range of investment costs in €/connection | Figure E
Functioneel ontwerp 5.0 Vesta MAIS | Annual operation and maintenance costs aquathermal storage | Jaarlijkse onderhouds- en beheerkosten WKO bronnen |  |  | 13115.7407 | eur/unit/year | Based on 'onderhoudspercentage WKO-bron' and the range of investment costs in €/connection | Figure E
Figure B
Figure C
Figure D
Figure E
Figure F